Riley Air Control Systems Pty Ltd.

VDH Series

High Performance/Stainless Steel

Volume Control Dampers

SPECIFICATION DATA

General

The VDH Series High Performance Volume Control Dampers provide highly efficient airflow control in air handling systems for aggressive atmosphere, with outside air control as its major application.  The VDH is a standard low leakage damper, available with ultra-low leakage feature (optional) and parallel or opposed blade configuration.

The damper frame, blades and linkages are made of stainless steel and guarantee long life with minimum maintenance.  Interlocking blade edges and spring steel side seals provide the basis for reduced (LOW) leakage.   Specially formed standard components and non-corrosive bearings conform to specifications required for high quality, low leakage, maximum rigidity and low operating torque.  This allows the use of smaller or fewer actuators.

Multiple sections are inter-connected with a solid drive shaft and provide, together with individually adjustable internal blade linkages, a positive connection for optimum close-off sealing.

Total damper design and close manufacturing tolerances of Blendair dampers result in LONG DAMPER LIFE, SMOOTH & RELIABLE CONTROL and ENERGY SAVING.

Features

- Spring stainless steel side seal minimises blade end leakage

- 9-breaks interlocking blades ensure rigidity and tighter close-off seal

- Ground stainless steel blade axles and ‘Delrin’ or Oilite (optional) bearings reduce friction and torque requirements, thus smaller actuators

- Rigid stainless steel construction resists corrosion in aggressive atmosphere and extends damper life

- Corrosive-resistant internal blade linkage allows easy maintenance and field adjustment and interchangeable components

- Clip-on seal (optional) allows field retro-fit

- Low leakage results in energy saving

VDH:   VOLUME CONTROL DAMPERS

DESCRIPTION & FUNCTION

The VDH Series Volume Control Damper is a HIGH PERFORMANCE low leakage damper, which provides efficient airflow control in air handling systems with aggressive atmosphere.   Airflow controls at sea-side, chemical industry and ‘Outside Air’ are its major applications.

The damper frame, blades and linkages are made of stainless steel and guarantee extra long life with minimum maintenance. Spring steel side seals and interlocking blade edges are the principle design features for low leakage.  Low friction internal blade linkages and blade bearings ensure extra low torque and smooth and efficient modulating operation, it allows the use of smaller or fewer actuators.

Dampers are installed  -  as standard  -  with horizontal blade orientation.  The opening, closing or modulation of the interconnected blades is effected by electric or pneumatic actuators initiated by control signals.  Dampers are also available for manual control setting.

MODELS

- VDH:	Low Leakage HIGH PERFORMANCE 	Stainless Steel Volume Control Damper for 	airflow control of air handling systems in 	corrosive atmosphere.Dampers are supplied 	with parallel  or opposed blade 	configuration. Ultra Low Leakage versions 	are available as option.

GUIDE SPECIFICATION (for the Engineer)

Volume Control Dampers installed for use in corrosive atmosphere or outside air application shall be of design and construction as the VDH  Model supplied by -Blendair, meeting requirements of LONG LIFE low leakage, extra low operating torque and smooth operation.

Dampers shall be solid Stainless Steel construction to prevent corrosion and minimise distortion or twisting during transit, installation and operation.  Blades shall be of 9-break design and of maximum 1200 mm length and shall be individually adjustable to obtain optimum air shut-

off.  Drive blades over 800 mm length shall be fitted with full-length stainless steel shaft to provide even torque distribution over blade length..  Blades shall be pivoting on 12.7 mm S/S shafts and ‘Oilite’ sintered bronze bearings.

DAMPER TYPES & APPLICATIONS

Dampers are supplied with two types of blade configuration:-

Parallel Blade  Dampers are constructed so that each blade rotates in parallel with or in the same direction as the blade next to it.  The rotation chages the direction of the airflow and can provide mixing and linear airflow characteristics, with only a small increase in airflow resistance.

Major control applications:

Return Air

Outdoor or Exhaust Air (w/o weather louvre or bird screen)

Bypass (w/o perforated baffle)

Two Positions or On/Off (all applications)

Outside Air

Opposed Blade Dampers are constructed so that adjacent blades rotate opposite to each other.  The rotation does not change the direction of the airflow, but it does increase the airflow resistance as the air is funnelled through a smaller opening.  Opposed blade dampers must be opened wider to obtain the same airflow as a parallel damper.

Major control applications:

Outdoor or Exhaust Air (with weather louvre or bird screen)

Coil Face

Bypass (with perforated baffle)

DAMPER ORDERING SPECIFICATION

VDH:   VOLUME CONTROL DAMPERS

Opposed Blade

Note:	For further information on damper selection refer to  Damper Selection Manual

DAMPER SIZING SPECIFICATION

Modules are supplied in the following standard sizes:

Single Module:	from 150mm x 150mm (min)

to 1200mm x 2400mm (max)

Size Increment:	50mm

Multi Modules:	available, for details refer to Sales or Factory

Note: .	When specifying damper sizes (width and height), quote internal duct dimensions.

SHIPPING WEIGHTS (Kg)

| Height (mm) | 200 | 400 | Width 600 | (mm) 800 | 1000 | 1200 |
| --- | --- | --- | --- | --- | --- | --- |
| 200 | 9 | 13 | 17 | 20 | 23 | 28 |
| 400 | 15 | 19 | 23 | 28 | 33 | 38 |
| 600 | 20 | 25 | 30 | 36 | 41 | 48 |
| 800 | 25 | 32 | 38 | 44 | 50 | 58 |
| 1000 | 32 | 38 | 45 | 53 | 59 | 68 |
| 1200 | 37 | 44 | 53 | 60 | 68 | 78 |
| 1400 | 42 | 50 | 60 | 68 | 77 | 88 |
| 1600 | 47 | 57 | 66 | 77 | 86 | 98 |
| 1800 | 53 | 63 | 74 | 84 | 95 | 105 |
| 2000 | 58 | 69 | 81 | 92 | 104 | 118 |
| 2200 | 64 | 76 | 88 | 100 | 112 | 128 |
| 2400 | 69 | 82 | 96 | 108 | 121 | 138 |

Note:	For weights of multi modules, add total weight by interpolating with above weight table.

SPECIFICATIONS  -  Construction

Materials & Finishes:

- Damper frame and blades are manufacture of 304 Stainless Steel sheet material (316 S/S optional).

Welds are wire brushed to clean off welding spatter and 	scale.

Damper Frame:

Standard Construction:	Press-formed 304 S/S

(316 S/S optional)

Material Thickness:	2.0 mm

Blades:

Standard Construction:	Press-formed 304 S/S

(316 S/S optional)

Material Thickness:	1.6 mm

Blade Seals:

Blade Ends:	Spring stainless steel continuous strips

(Side Seal)

Blade Edge:	Clip-on,  (optional)

Blade Bearings:

Bearing Types:	‘Delrin’ (standard) for operating temperature -40 to +100 degree C and horizontal blade mounting.

‘Oilite’ sintered bronze bearings (optional) for high temperature application (max 200 degree C) and vertical blade mounting (optional)

Blade Axle & Drive Shaft:

Material:	12.7 mm diameter ground 303/316 (optional) Stainless Steel

Blade Axles:	Blades are fastened to 50 mm long axles with special self-locking, shake-proof bolts.

Drive Shaft:	Drive Blade is fitted with 225 mm long drive shaft that extends outside the frame for external motor mounting, but is retracted for protection purpose during transit.

Dampers with over 800 mm blade length or over 0.6 m2 are fitted with full-length drive shaft.

Manual Drive Hardware:

For manual operation, dampers are fitted with adjustable and lockable Quadrant and supplied without side seals.

Blade Linkage Hardware:

Linkage Bracket:	Press-formed 304 S/S (316 S/S optional) with interchangeable pivots and bushes

Linkage Connection Rod:

8.00 mm 303 S/S (316 S/S optional)

Set Screws & Blade Mounting Bolts:

303 S/S (316 S/S optional)

VDH:   VOLUME CONTROL DAMPERS

Blade Orientation:

Dampers are available in two blade orientations (to be specified by customer):   Parallel and Opposed.

SPECIFICATIONS  -  Technical

Maximum Pressure Differential:

1.5 kPa (6 Inch WC)

Maximum Approach Velocity:

20 m/sec (4000 fpm)

Temperature Range:

-40  to  +100 degree C (standard)

-40  to  +93 degree C (with  seal)

Leakage Characteristics:

LOW LEAKAGE CURVE

SPARE PARTS

| Model No. | Description |
| --- | --- |
| VDH-01 | Large linkage 304/316 |
| VDH-02 | Medium linkage 304/316 |
| VDH-03 | Small linkage 304/316 |
| VDH-04 | Olite bearing |
| VDH-05 | Blade axle 304/316 |
| VDH-06 | Axle lock screw |
| VDH-07 | Nut bolt drive shaft |

Note:	Other parts may be available on special request

INSTALLATION

Important!	Improperly installed dampers prevent blades from sealing (see sketch below).  Gaps between the blades and frame indicate that the damper is installed ‘out of square’ or ‘out of flat’.  These misalignments will cause increased leakage and can result in blade-to-linkage bind or non-closure of blades, thus overloading the damper actuator or render it inoperative.

Installation Hints:

1.	Always observe and follow instructions on label affixed to damper.

2.	Before installation, ensure that damper is not damaged and blades operate freely.

3.	Allow sufficient room on side of damper for mounting of actuator.

4.	Install damper ‘square and flat’ as per warning above.  Carry out final field adjustment to blade linkages, ensuring that all damper close tightly and tighten all sets-crews

5.	Perform trial run of damper & actuator assembly, before attaching other end of duct work to damper.

OTHER DAMPER PRODUCTS

- Volume Control Dampers:

Low & Ultra Low Volume Control, Smoke Spill Damper, Min/Max Damper, Face & Bypass Damper, Zone Damper, Non-Return & Barometric Damper

- Fire Dampers:

Multi-Blade Fire Damper, Single Blade Fire Damper, Circular Fire Damper, Volume-Fire Damper, Ceiling Fire Damper, Curtain Fire Damper

- Sub Ducts

- Actuators & Damper Accessories:

Head Office:	Riley Air Control Systems Pty. Ltd.

3/78-80 Bellingara Road

Miranda  NSW   2228

Phone: (02) 9544 8854

Fax:(02) 9544 8545

A.B.N. 80 003 437 732